[image: image60.png]R e e N Huazheng




[image: image66.png]Huazheng





HZ-IV 

Transformer LV Short-circuit Impedance Tester
                        [image: image1.png]



Huazheng Electric Manufacturing(Baoding) Co.,Ltd

Dear user:

Thank you for choosing HZ-IV Transformer LV Short-circuit Impedance Tester.

     We hope that this instrument can make your work easier and more enjoyable, so that you can get the feeling of office automation in the test and analysis work.

  Before using the instrument, please read this manual, and operate and maintain the instrument according to the manual to prolong its service life.

"Just a light press, the test will be completed automatically" is the operating characteristics of this instrument.

     If you are satisfied with this instrument, please tell your colleagues; if you are not satisfied with this instrument, please call (0312) 6775656 to tell you to serve you at all times-Baoding Huazheng Electric Manufacturing Co., Ltd., our company will definitely make you satisfied !

Contents

1I. Technical Parameters


1II. Characteristics


2III.Wiring Diagram


2IV. Operating Instructions:


9V.Impedance Formula


11VI.Packing List


11VII. Order and Service




Transformer LV Short-circuit Impedance Tester applies to LV load impedance test during delivery, overhaul, trial test and handover test of power transformers (single phase or three-phase).

It tests the short-circuit impedance (%) of power voltage on site and compares it with the value indicated on the nameplate or the factory default to find out any defects including but not limited to winding displacement or deformation due to currents from major failure during transformation, installation or operation following the delivery test. (The short circuit change shall be considered as significant if it exceeds ± 3% as specified in China International Conference on Electricity Distribution 2000 (“CICED 2000”)).

Transformer LV Short-circuit Impedance Tester is not provided with an external voltage regulator and adopts the primary connection mode. It begins the three-phase testing and calculates impedance error percentage automatically when the parameter is entered and provides intuitive results. This is a rapid tester which detects winding deformation of transformers on site.

I. Technical Parameters

	Scope of voltage measurement: 5~400V
	Accuracy of measurement: 0.2d

	Scope of current measurement: 0.1~20A
	Operating power: AC220V±10%

	Power frequency: 50Hz
	Operating temperature: -10℃~50℃

	Ambient humidity: ≤85%RH
	Net weight: 6kg


II. Characteristics

1.The tester is supplied with AC220V low voltage power to provide current for AB, BC and CA high voltage windings of the transformer automatically; collects data simultaneously and; calculates impedance error percentage automatically with intuitive testing results;

2.The tester completes the three-phase testing automatically in the primary connection mode other then inversed connection with the testing wire;
3. The tester allows either single phase testing or three-phase testing both manually and automatically;

4. The tester achieves output current limit applicable to test item with any impedance;

5. The test item can be measured without an external voltage regulator;

6.The tester functions in measuring zero sequence impedance;

7. The tester functions in measuring inductance;

8. The tester has a large LCD display with a menu in Chinese. Operation are facilitated based on the notes on the display; and

9.The tester enables printing and storage and is featured with high testing accuracy, high automation, small in size and light weight.

III.Wiring Diagram

● Fig. A depicts the wiring of a single phase transformer
● Fig. B depicts the wiring of a three-phase dual-winding transformer

	[image: image2.png]


[image: image61.png]R e e N Huazheng



  
Fig. A
	[image: image62.png]R e e N Huazheng



[image: image3.png]



Fig. B


● 
Wiring of the three-phase dual-winding transformer is consistent with the selected position to be measured. If a High-Low position is selected for measurement, the testing wire should be connected to the HV side while the LV side is under short circuit; the remaining wires are under open circuit. If a High-Medium position is selected, the testing wire should be connected to the HV side while the medium voltage side is under short circuit; the remaining wires are under open circuit. If a Medium-Low position is selected, the testing wire should be connected to the medium voltage side while the LV side is under short circuit; the remaining wires are under open circuit.

● 
The section of short circuit wire should be no less than 10 mm2 (bare copper wire is preferred). Such wire should be in good contact; otherwise it will affect the accuracy of testing data.

IV. Operating Instructions:

1. The interface shows when the tester is powered on: (Interface 1)

	Welcome


Interface 1

2. Push down ENT to enter into the parameter setting interface: (Interface 2)

	Rated capacity: 
	50,000 KVA

	Rated voltage: 
	110.00 KV

	Nameplate impedance: 
	17.98 %

	Tapping position:
	09

	Measurement position: 
	High-Low

	Item No.:
	10

	Testing temperature: 
	+20℃

	[image: image63.png]R e e N Huazheng



[image: image64.png]R e e N Huazheng



Note: 
: Select, Ent: Test, Esc: Exit


Interface 2

3. 
Enter the data on the transformer nameplate according to notes on the display. Push down ↑↓ to select a line. Push down ← to delete a digit towards the left. Push down the numeric keys to enter a digit. If negative testing temperature is needed, first push down ← to delete the digit, then push down ↓ to adjust a positive/negative sign; enter the temperature data and push down ENT to go to the interface below: (Interface 3)

Note: 

● 
The input of rated voltage should be consistent with the tapping position.

● 
If the single-phase process is used for a three-phase transformer, the data to be entered should be 1/3 of the rated capacity.

	Test

	Single Phase  Three-phase  Zero Sequence Impedance

	Note: ← →: Select, Ent: OK, Esc: Exit


Interface 3

4. Select a single phase transformer or a three-phase transformer to be measured.

● 
Measurement of a single phase transformer:
Connect the testing wire between the tester and the transformer as shown in Fig. A of the wiring diagram. Enter the parameter. Select Single Phase in Interface 3. Push down ENT and it will show as follows: (Interface 4)

	Single Phase Test

[image: image65.png]R e e N Huazheng



UAN: V
IAN: A

ZK%: %
△ZK%: %

Frq: Hz
LAN: mH

	Note: Ent: Start,
Esc: Exit


Interface 4

Push down ENT to start measurement. The testing results will be shown on the display. The interface will show as follows: (Interface 5)

	Single Phase Test

[image: image66.png]UAN: x.xxx  V     IAN: x.xxx    A

ZK%: xxx.x  %     △ZK%: - x.xxx %

Frq: 50.00  Hz      LAN:  x.xxx    mH              

Note: Ent: Lock, Esc: Exit


Interface 5

③ 
Push down ENT to stop when the desired value of testing data is achieved. The testing data will be locked.

④ 
After locking the data, push down Print to directly print the test report. 

	Item No.: 10

Tester by:

Test date:

Rated capacity Sn: 50,000 KVA

Rated voltage Un: 110.00 KV

Nameplate impedance ZK%: 17.89%

Tapping position: 09

Testing position: High-Low

Measurement connection: Single phase

Voltage applied UAN: x.xxx V

Current applied IAN: x.xxx A    

Measured impedance ZK%: x.xxx  %

Impedance error △ZK%:- x.xxx  %

Test frequency Frq: 50.00Hz

Measured inductance LAN: x.xxx mH


⑤ Push down SAVE. An “ALL DONE” notice will show at the lower right corner. If it is stored in the U-disk, please return to the “Welcome” interface when the tester is powered on. Press SAVE and the display will show all records saved. Select a record, insert the U-disk and press SAVE to save it in the U-disk. An “ALL DONE” notice will show at the lower right corner of the display.

● 
Measurement of a three-phase transformer – manual measurement:

① 
Connect the testing wire between the tester and the transformer as shown in Fig. B of the wiring diagram. Enter the parameter. Select Three-phase in Interface 3. Push down ENT and it will show as follows: (Interface 6)
	Test

	Single Phase
Three-phase
Zero Sequence Impedance

Manual
Auto

	Note: ← →: Select, Ent: OK, Esc: Exit 


Interface 6

② 
Push down ← → to select the Manual or Auto mode. If Manual is selected, push down ENT to show three connection modes of the transformer: Y/△, Y/Y, △/Y, as shown below: (Interface 7)

	Test

	Single Phase
Three-phase
Zero Sequence Impedance

Manual
Auto

	Note: ← →: Select, Ent: OK, Esc: Exit 


Interface 7

Notes:
a. 
The connection mode in Interface 7 should be selected based on the connection group of the transformer terminal.

b. 
Note: For the Medium-Low position of the three-phase three-winding transformer, Y denotes medium voltage and the low voltage side is under short circuit. Y/△ or Y/Y may be selected without allowing the connection mode of low voltage.

c. 
Push down ← → to select the connection mode of the transformer. If △/Y is selected, two different connection modes of △ mode will show: AZ-BX-CY or AY-BZ-CX to be determined by user according to conditions of the test item.

③After selecting, push down ENT to go to the interface below: (Interface 8)

	AB  BC  CA     Manual Three-phase

	UAB:    V         IAB:     A

UBC:    V         IBC:    A

UCA:    V         ICA:    A

	Note: Ent: Start, Esc: Exit


Interface 8

Push down ← → to select the current applied AB, BC or CA phase. If AB phase is selected, push down ENT to measure the voltage and current of AB phase, as shown below (Interface 9):

	AB   BC   CA      Manual Three-phase

UAB: x.xxx V       IAB: x.xxx A

UBC:       V       IBC:       A

UCA:       V       ICA:       A

Note: Ent: Lock, Esc: Exit      Testing


Interface 9

⑤Push down Ent to lock the data. Push down Ent again to select the status of BC phase. Push down ← → to select BC phase, as shown below (Interface 10):

	AB   BC   CA      Manual Three-phase

	UAB: x.xxx V       IAB: x.xxx A

UBC:       V       IBC:       A

UCA:       V       ICA:       A

	Note: Ent: Start, Esc: Exit      Testing


Interface 10
⑥ 
Push down ENT to measure the voltage and current of BC phase, as shown below: (Interface 11)

	AB   BC   CA       Manual Three-phase

	UAB: x.xxx V       IAB: x.xxx A

UBC: x.xxx V       IBC: x.xxx A

UCA:       V       ICA:       A

	Note: Ent: Lock, Esc: Exit      Testing


Interface 11
⑦ 
The testing procedure of CA phase is the same as above. When the data of CA phase is locked, the tester will give an integrated calculation for the testing data of manual single phase for three times automatically. The display will show the impedance testing results and provide a printed report after two seconds. 

An interface will show as follows: (Interface 12)
	AB   BC   CA        Manual Three-phase

	ZK%a: x.xxx %            ZK%b: x.xxx %  

ZK%c: x.xxx %

ZK%: x.xxx  %75°       △ZK%:- x.xxx % 

LAN: x.xxx mH            LBN: x.xxx mH

LCN: x.xxx mH 

	Note: Esc: Exit


Interface 12

⑧ 
Push down Print to directly print the test data report (the same with subsequent three-phase auto report).

⑨ 
Push down SAVE to save it in the tester. An “ALL DONE” notice will show at the lower right corner. If it is stored in the U-disk, please return to the “Welcome” interface when the tester is powered on. Press SAVE and the display will show all records saved. Select a record, plug in the U-disk and press SAVE to save it in the U-disk. An “ALL DONE” notice will show at the lower right corner of the display.
⑩ 
Push down ESC to return to the parameter setting interface from the testing interface. The manual single phase measurement of a three-phase transformer ends.

● 
Measurement of a three-phase transformer – three-phase auto measurement:
① 
Push down Ent after entering the data. Select the three-phase transformer, as shown below: (Interface 13)

	Test

Single Phase     Three-phase   Zero Sequence Impedance

Note: ← →: Select, Ent: OK, Esc: Exit


Interface 14

Push down Ent. Press ← → to select Auto mode, as shown below: (Interface 14)

	Test

	Single Phase        Three-phase     Zero Sequence Impedance

Manual        Auto

	Note: ← →: Select, Ent: OK, Esc: Exit


Interface 14

③ Push down ENT. Press ← → to select the connection mode, as shown below: (Interface 15):

	Test

	Single Phase       Three-phase     Zero Sequence Impedance

Manual       Auto
Y/△        Y/Y       △/Y

	Note: ← →: Select    Ent: OK,  Esc: Exit


Interface 15

Notes:

a. 
The connection mode in Interface 15 should be selected based on the connection group of the transformer terminal.

b. 
Note: For the Medium-Low position of the three-phase three-winding transformer, Y denotes medium voltage and the low voltage side is under short circuit. Y/△ or Y/Y may be selected without allowing the connection mode of low voltage.  

c. 
Push down ← → to select the connection mode of the transformer. If △/Y is selected, two different connection modes of △ mode will show: AZ-BX-CY or AY-BZ-CX to be determined by user according to conditions of the test item.

④ 
Push down ENT to go to the interface below: (Interface 16)

	AB   BC   CA        Auto Three-phase

	UAB:      V       IAB:       A

UBC:       V       IBC:       A

UCA:       V       ICA:       A

	Note: Ent: Start, Esc: Exit 


Interface 16

⑤ 
Push down Ent to measure. The tester applies current to the windings of AB, BC and CA phases, collects data automatically and locks the measurements of three phases in turn. After measuring, the tester calculates impedance error automatically.

The display will show the measurements: (Interface 17)

	AB   BC   CA         Auto Three-phase

	ZK%a: x.xxx %            ZK%b: x.xxx %  

ZK%c: x.xxx %

ZK%: x.xxx  %75°       △ZK%:-x.xxx % 

LAN: x.xxx mH            LBN: x.xxx mH

LCN: x.xxx mH

	Note: Esc: Exit


Interface 17

Push down Print to directly print the test report below:


Voltage applied UBC: x.xxx   V 


Current applied ICA: x.xxx   A 

	Measured impedance ZKab%: x.xxx % 

Impedance error △ZKab%: - x.xxx % 

Measured impedance ZKbc%: x.xxx  % 

Impedance error △ZKbc%: - x.xxx% 

Measured impedance ZKca%: x.xxx %

Impedance error △ZKca%: - x.xxx% 

Measured impedance ZK%: x.xxx % 

Impedance error △ZK%: - x.xxx % 

Measured inductance LAN: x.xxx   mH

Measured inductance LBN: x.xxx   mH

Measured inductance LCN: x.xxx   mH


⑦Push down SAVE to save it in the tester. An “ALL DONE” notice will show at the lower right corner. If it is stored in the U-disk, please return to the “Welcome” interface when the tester is powered on. Press SAVE and the display will show all records saved. Select a record, plug in the U-disk and press SAVE to save it in the U-disk. An “ALL DONE” notice will show at the lower right corner of the display.
● 
Measurement of a three-phase transformer – single phase measurement:
If the single-phase process is used for a three-phase transformer, the data to be entered should be 1/3 of the rated capacity.

The connection and operating mode should be the same with that of a single-phase transformer.

● 
Measurement of zero sequence impedance: When the zero sequence impedance is measured, the connection mode should be in such a manner that the HV three phases should be in parallel while the low voltage is under short circuit. Operations are provided as follows:

① 
Select Zero Sequence Impedance in Interface 3 as follows: (Interface 18)
	Test

Single Phase
Three-phase
Zero Sequence Impedance

Note: ← →: Select, Ent: OK, Esc: Exit


Interface 18

②Push down Ent to measure. The measurement results are shown below: (Interface 19)

	Zero Sequence Impedance

	UAN:x.xxx   V      IAN: x.xxx   A    

ZK: x.xxx   Ω

	Note: Ent: Lock, Esc: Exit


Interface 19

③Push down Ent to lock. Push down Print to directly print the test report below:

	Item No.: 10

Tested by:

Test date:

Rated capacity Sn :50000 KVA

Rated voltage Un :110.0 KV

Voltage applied UAB: x.xxx   V 

Current applied IAB: x.xxx   A 

Zero sequence impedance: x.xxx   %


④Data storage and storage in the U-disk are the same with that of impedance testing.

V.Impedance Formula

(1) 
For single phase transformer: Calculations should be based on the rated capacity for the level to be measured
Y/△ connection: 
[image: image4.wmf]K

Z

% = 
[image: image5.wmf]´

1000

3



 EMBED Equation.3  [image: image6.wmf]%

100

2

´

´

N

N

K

K

U

S

I

U


Impedance error: △ZK% = (ZK′%—ZK%)÷ZK′%

Wherein: 
[image: image7.wmf]K

I

-Short-circuit current during testing (A)


[image: image8.wmf]K

U

-Short-circuit voltage during testing (V)


[image: image9.wmf]N

U

- Rated voltage (the rated voltage for the line during testing) (KV)


[image: image10.wmf]K

Z

%-LV short-circuit impedance percentage


[image: image11.wmf]K

Z

¢

%-Short-circuit impedance percentage indicated on the nameplate or in the delivery test report

(2) 
Three-phase transformer:  

1.
Y/△ or Y/Y connection: Calculations should be based on the rated capacity


[image: image12.wmf]A

Z

% =
[image: image13.wmf]%

100

2000

1

2

´

´

-

+

´

N

N

BC

AC

AB

AC

AB

BC

BC

AB

AC

BC

AC

AB

U

S

I

I

I

I

I

U

I

I

U

I

I

U



[image: image14.wmf]B

Z

% =
[image: image15.wmf]%

100

2000

1

2

´

´

-

+

´

N

N

BC

AC

AB

BC

AB

AC

AC

AB

BC

BC

AC

AB

U

S

I

I

I

I

I

U

I

I

U

I

I

U



[image: image16.wmf]C

Z

% =
[image: image17.wmf]%

100

2000

1

2

´

´

-

+

´

N

N

BC

AC

AB

AC

BC

AB

BC

AB

AC

AB

AC

BC

U

S

I

I

I

I

I

U

I

I

U

I

I

U



[image: image18.wmf]%

K

Z

=
[image: image19.wmf](

)

3

/

%

%

%

C

B

A

Z

Z

Z

+

+

             

Impedance error: △ZK% = (ZK′%—ZK%)÷ZK′%

Wherein: 
[image: image20.wmf]AB

I

+
[image: image21.wmf]BC

I

+
[image: image22.wmf]CA

I

-Short-circuit current during testing (A);


[image: image23.wmf]AB

U

, 
[image: image24.wmf]BC

U

, 
[image: image25.wmf]CA

U

-Short-circuit voltage during testing (V)


[image: image26.wmf]N

U

-Rated voltage (rated voltage for the line during testing) (KV)


[image: image27.wmf]N

S

-Rated capacity (KVA)


[image: image28.wmf]K

Z

%-LV short-circuit impedance percentage


[image: image29.wmf]K

Z

¢

%-Short-circuit impedance percentage indicated on the nameplate or in the delivery test report

2.
△/Y connection: (a, b and c at the secondary side should be short circuited)

(1) 
For AZ-BX-CY connection: Calculations should be based on the rated capacity


[image: image30.wmf]AZ

Z

% =
[image: image31.wmf]´

60

1



 EMBED Equation.3  [image: image32.wmf](

)

(

)

2

2

2

4

N

N

AC

AB

BC

BC

AC

AB

BC

AB

AC

AC

BC

AB

BC

AB

AC

BC

AB

AC

AB

BC

AC

BC

AB

BC

AB

AC

U

S

I

I

U

I

I

U

I

I

U

I

I

I

I

I

I

U

U

I

I

U

I

I

U

I

I

U

´

ú

ú

û

ù

ê

ê

ë

é

-

-

-

-

-



[image: image33.wmf]BX

Z

% =
[image: image34.wmf]´

60

1



 EMBED Equation.3  [image: image35.wmf](

)

(

)

2

2

2

4

N

N

BC

AB

AC

AB

AC

BC

BC

AC

AB

AC

BC

AB

BC

AC

AB

BC

AC

BC

AB

AC

AC

AB

BC

BC

AC

AB

U

S

I

I

U

I

I

U

I

I

U

I

I

I

I

I

I

U

U

I

I

U

I

I

U

I

I

U

´

ú

ú

û

ù

ê

ê

ë

é

-

-

-

-

-



[image: image36.wmf]CY

Z

% =
[image: image37.wmf]´

60

1



 EMBED Equation.3  [image: image38.wmf](

)

(

)

2

2

2

4

N

N

BC

AB

AC

BC

AC

AB

AC

AB

BC

AC

BC

AB

AC

AB

BC

AC

AB

BC

AB

AC

AC

BC

AB

AC

AB

BC

U

S

I

I

U

I

I

U

I

I

U

I

I

I

I

I

I

U

U

I

I

U

I

I

U

I

I

U

´

ú

ú

û

ù

ê

ê

ë

é

-

-

-

-

-


(2) 
For AY-BZ-CX connection: Calculations should be based on the rated capacity


[image: image39.wmf]AY

Z

% =
[image: image40.wmf]´

60

1



 EMBED Equation.3  [image: image41.wmf](

)

(

)

2

2

2

4

N

N

BC

AB

AC

BC

AC

AB

AC

AB

BC

AC

BC

AB

AC

AB

BC

AC

AB

BC

AB

AC

AC

BC

AB

AC

AB

BC

U

S

I

I

U

I

I

U

I

I

U

I

I

I

I

I

I

U

U

I

I

U

I

I

U

I

I

U

´

ú

ú

û

ù

ê

ê

ë

é

-

-

-

-

-



[image: image42.wmf]BZ

Z

% =
[image: image43.wmf]´

60

1



 EMBED Equation.3  [image: image44.wmf](

)

(

)

2

2

2

4

N

N

AC

AB

BC

BC

AC

AB

BC

AB

AC

AC

BC

AB

BC

AB

AC

BC

AB

AC

AB

BC

AC

BC

AB

BC

AB

AC

U

S

I

I

U

I

I

U

I

I

U

I

I

I

I

I

I

U

U

I

I

U

I

I

U

I

I

U

´

ú

ú

û

ù

ê

ê

ë

é

-

-

-

-

-



[image: image45.wmf]CX

Z

% =
[image: image46.wmf]´

60

1



 EMBED Equation.3  [image: image47.wmf](

)

(

)

2

2

2

4

N

N

BC

AB

AC

AB

AC

BC

BC

AC

AB

AC

BC

AB

BC

AC

AB

BC

AC

BC

AB

AC

AC

AB

BC

BC

AC

AB

U

S

I

I

U

I

I

U

I

I

U

I

I

I

I

I

I

U

U

I

I

U

I

I

U

I

I

U

´

ú

ú

û

ù

ê

ê

ë

é

-

-

-

-

-



[image: image48.wmf]%

K

Z

=
[image: image49.wmf](

)

3

/

%

%

%

C

B

A

Z

Z

Z

+

+


Impedance error: △ZK% = (ZK′%—ZK%)÷ZK %

Wherein: 
[image: image50.wmf]AB

I

+
[image: image51.wmf]BC

I

+
[image: image52.wmf]CA

I

-Short-circuit current during testing (A);


[image: image53.wmf]AB

U

, 
[image: image54.wmf]BC

U

, 
[image: image55.wmf]CA

U

-Short-circuit voltage during testing (V)


[image: image56.wmf]N

U

-Rated voltage (rated voltage for the line during testing) (KV)


[image: image57.wmf]N

S

-Rated capacity (KVA)


[image: image58.wmf]K

Z

%-LV short-circuit impedance percentage


[image: image59.wmf]K

Z

¢

%-Short-circuit impedance percentage indicated on the nameplate or in the delivery test report

VI.Packing List

	No.
	Item
	Qty

	1
	Private wire
	1

	2
	Power wire
	1

	3
	Ground wire
	1

	4
	Line box
	1

	5
	Fuse
	1

	6
	Typing paper
	1


VII. Order and Service

1.A one-year free warranty is given to products subject to quality problems since the date of manufacture; materials costs will be charged for any damage due to other causes. Costs of repair and maintenance will be only charged if it is out of the free warranty.

2.We provide lifetime maintenance and technical services for the products.

3.Please contact us immediately upon discovery of any abnormality in the tester . We will provide the most convenient solution for you. DO NOT disassemble the tester!

Single-phase transformer test








Transformer LV Short-circuit Impedance Tester








The wiring of a single phase transformer








Three-phase transformer test








Transformer LV Short-circuit Impedance Tester








The wiring of a three-phase dual-winding transformer












_1234567905.unknown

_1234567921.unknown

_1234567929.unknown

_1234567933.unknown

_1234567937.unknown

_1234567941.unknown

_1234567943.unknown

_1234567944.unknown

_1234567945.unknown

_1234567942.unknown

_1234567939.unknown

_1234567940.unknown

_1234567938.unknown

_1234567935.unknown

_1234567936.unknown

_1234567934.unknown

_1234567931.unknown

_1234567932.unknown

_1234567930.unknown

_1234567925.unknown

_1234567927.unknown

_1234567928.unknown

_1234567926.unknown

_1234567923.unknown

_1234567924.unknown

_1234567922.unknown

_1234567913.unknown

_1234567917.unknown

_1234567919.unknown

_1234567920.unknown

_1234567918.unknown

_1234567915.unknown

_1234567916.unknown

_1234567914.unknown

_1234567909.unknown

_1234567911.unknown

_1234567912.unknown

_1234567910.unknown

_1234567907.unknown

_1234567908.unknown

_1234567906.unknown

_1234567897.unknown

_1234567901.unknown

_1234567903.unknown

_1234567904.unknown

_1234567902.unknown

_1234567899.unknown

_1234567900.unknown

_1234567898.unknown

_1234567893.unknown

_1234567895.unknown

_1234567896.unknown

_1234567894.unknown

_1234567891.unknown

_1234567892.unknown

_1234567890.unknown

