[image: image14.png]R e e N Huazheng



                                            
[image: image17.png]Huazheng





On-line Monitoring System of HZGC-1210 Transformer Oil Chromatography
User Manual 

Huazheng Electric Manufacturing (Baoding) Co., Ltd

Dear user:

Thank you for choosingOn-line Monitoring System of HZGC-1210 Transformer Oil Chromatography.

     We hope that this instrument can make your work easier and more enjoyable, so that you can get the feeling of office automation in the test and analysis work.

  Before using the instrument, please read this manual, and operate and maintain the instrument according to the manual to prolong its service life.

"Just a light press, the test will be completed automatically" is the operating characteristics of this instrument.

     If you are satisfied with this instrument, please tell your colleagues; if you are not satisfied with this instrument, please call (0312) 6775656 to tell you to serve you at all times-Baoding Huazheng Electric Manufacturing Co., Ltd., our company will definitely make you satisfied !

 Application
The on-line monitoring system of HZGC-1210 transformer oil chromatogram is used in the on-line analysis and fault diagnosis of dissolved gas in power transformer oil. It is suitable for oil-immersed high voltage equipment in all kinds of voltage grade like power oil filled transformer, electric-arc furnace transformer, reactor and transformer. 
Safety Procedure
For those personnel who are responsible for the installation, operation, maintenance and repair of the equipment
◆ Must have relevant professional qualifications
◆ Must follow each line of instructions 
◆ Do not play games or browse the web in the data processing server. 
◆ In order to avoid unnecessary conflict, do not install additional software in the data processing server. 
◆Unprofessional operations or misuse would lead to：

◆ Shorten the equipment lifespan and influence monitoring accuracy
◆ Damage the equipment and other equipment of the user
◆ Give rise to fatal damage
Brief Introduction

The on-line monitoring system of HZGC-1210 type transformer oil chromatogram can realize following functions: automatic circulatory cleaning, oil in, oil and gas separation, sample analysis, data processing and real-time alarm; It could quickly online monitor the content and growth of fault gas dissolved in the oil of oil-immersed power HV equipment transformer like transformers. Through fault diagnosis expert system, it could earlier forecast the hidden trouble of equipment failure, avoiding equipment accidents, so as to reduce the heavy losses and improve the reliability of equipment operation. As a new generation of products in the field of oil chromatogram on-line monitoring, the system will provide stable and reliable solutions for power transformer to realize on-line remote DGA analysis. Therefore, it is the forceful guarantee for the implementation of state overhaul of power system.

HZGC-1210 system is designed on the base of all the advantages of on-line monitoring of oil chromatogram at home and abroad. So the system has obvious advantages in the aspects of the stability, reliability and accuracy. 
♦ On-line testing the concentration and growth rate of H2、CO、CO2、CH4、C2H4、C2H2、C2H6
♦ The method of quantitative cleaning and circulatory sampling could truly reflect the state of gas dissolved in oil.
♦ Oil-gas separation is safe and reliable without any pollution. The users could choose to discharge the transformer oil or not. 
♦ It adopted dedicated composite chromatographic column to improve the degree of separation of gas component.
♦ It adopted imported detector to enhance the sensitivity of testing hydrocarbon gases.
♦ The gas detection technique has high stability and precision with ± 10% error range.
♦ Mature and reliable as the communication mode is, it adopted standard networking protocols and could support remote data transmission. 
♦ Data collection, adopted the oversampling technology Δ - ∑ analog-digital converter with 24-bit resolution and automatic calibration, is highly reliable. 
♦ Diverse data display and inquiry modes could provide report and trend chart. The storage life of historical data is 10 years.  
♦ It has strong environmental adaptability, widely used in cold, hot, high humidity and high altitude areas. 
♦ The performance of anti-interference is outstanding. The electromagnetic compatibility could meet GB/T17626 and IEC61000 standard. 

♦ It offered 2 level of alarming set. Alerting signal could spread widely. 
♦ Open database could access to LAN of electric system. 
In addition, HZGC-1210 system uses modular design with the application of high-performance embedded processors, making chromatography online monitoring system more stable and reliable. It has the following features:

♦ It has faster analysis cycle which can be set by users themselves. The minimum monitoring cycle is 40 to 60 minutes. We recommend setting 24 hours as an inspection cycle;
♦ It takes only 10 minutes to separate oil and gas. It uses special environmental adaptation technology to eliminate any change of gas distribution coefficient caused by the temperature and humidity changes. 
♦Analyzed oil sample adopted the technique of degassing and buffering, removing the mingled bubble in oil sample of reinjection transformer. The technique of multilayer isolated reinjection oiling (return oiling) could guarantee the carried gas would not be taken into the transformer. 
♦ The minimum limit of detection of C2H2 can reach 0.1-0.5 μ L/L. 
♦ It adopted double circuit and multi-mode thermostatic control with ± 0.1 ℃ temperature control accuracy. The device is equipped with industrial air conditioning which has the function of automatic constant temperature control. 
♦ The embedded processor control system is multi-function, combining oil-gas separation, data acquisition, chromatographic analysis, concentration calculation, data alarming, and equipment condition monitoring. Cases like data loss would be avoided, greatly improving the reliability and stability of the system. 
♦ Functional interface circuit adopted opto-isolator to further improve the ability of anti-interference. 
♦ Via Ethernet, it could realize full-digital and remote data transmission, parameter setting and control. 
♦ It improves the function of fault diagnosis, applying modified three ratio method, David trigonometry and cube graphic method to draw the diagnosis result;

♦ It strengthens self-inspection and adds the function of remote maintenance and alarming for equipment abnormality 

♦ It supports 61850 communication protocol, providing networking for monitoring equipment of the same kind, so that it can realize concentrated remote diagnosis in a certain area.   
♦ The system adopted 19 standard case and high-integrated modular design, which is easy to install and maintain with user-friendly operation.

♦ With wide expandability, it could integrate with other monitoring device conveniently. 

♦ The design of non-cylinder saves the time and money to change the carrier gas every year so that after sale maintenance would be much easier. Without high pressure vessel nearby, transformers would be safer, free from any potential risk. 

The composition of on-line monitoring system of HZGC-1210 transformer oil chromatography 
The on-line monitoring system of HZGC-1210 transformer oil chromatogram can be independently operated by the field monitoring host. The field monitoring host includes four high-integrated modules and auxiliary units. Those are chromatographic data collection and processing module, gas-oil separation module, gas detection module and air source module. The chromatograph data collection and processing module contains data acquisition unit, field control processing unit, communication control unit and 61850 communication protocol, etc.; The oil-gas separation module contains cycled sample acquisition unit, quantitative oil sample unit, return unit of oil sample processing and degassing / collecting unit, etc.; The gas detection module contains gas separation unit, constant temperature/current control unit and gas detection unit, etc.; Air source module contains gas generating unit, gas storage unit, purification unit, pressure control and alarm unit, etc.; Auxiliary units including transformer interfaces, oil pipe, communication cables and power cables. 

If you do not upload data and alarm value directly by 61850 communication protocol, you shall install computer and monitoring software in master-control room so that you could directly monitor running status of equipment in the main control room. 

The working principle of on-line monitoring HZGC-1210 transformer oil chromatography 
When on-line monitoring system of HZGC-1210 transformer oil chromatogram is working, oil sample collection unit would start oil-way circulation to dispose the dead oil in connection pipe,  then try to set the quantity of oil sample; Oil-gas separation unit would quickly separate the dissolved gas from transformer oil and deliver it to the sample loop of six-way valve for auto injection; prompted by the carrier gas, the sample gas would be separated through chromatographic column, and flow into gas detector in order; data acquisition unit shall complete conversion and acquisition of AD data. The embedded processing unit shall be responsible for the storage, calculation and analysis of the collected data. In addition, the embedded processing unit would upload the data to data procession server (installed in the master control room) via 100m Ethernet interface. Finally, the monitoring and early warning software would start data processing and fault analysis. 

[image: image1.png]‘Sample gas channel

gas separation The mou

system

Pre-column
pressure gauge  Regulator valve

«:Garrier gas

Detector

Mierocontrofier
circuit




Pic 2.3 Schematic diagram of HZGC-1210 system principle

2.3 The main parameter of on-line monitoring system of HZGC-1210 transformer oil chromatography 

	No.
	Parameter name
	value

	1
	Model 
	HZGC-1210

	2
	Working temperature
	-40℃～＋70℃

	3
	Working humidity
	Relative humidity5～95%（interior of device shall be free from condensation and ice.）

	4
	Atmospheric pressure
	70kPa～110kPa 

	5
	Power supply
	AC 220 V±10% ， 50Hz

	6
	Monitoring content
	Monitor H2、 CO、 CO2、 CH4、 C2H4、 C2H2、 C2H6 in the aspects of Total hydrocarbon, relative growth rate and absolute growth value. (optional to choose the oil with few water content)

	7
	Analysis and diagnosis
	Conduct analysis and diagnosis for the monitoring data via improved three-ratio method, Duval's triangle and cubic graphic method. Provide the original chromatography. 

	8
	Minimum detection period
	Range between 40 and 60min, up to user’s settings. default 24 hours

	9
	Sampling method
	Circulatory sampling would reflect the air status in transformers precisely. 

	10
	Oil-gas separation method
	vacuum degassing method

	11
	Data storage life
	≥ 10 years

	12
	Equipped carrier gas 
	gas generator 

	13
	Monitored gas
	Range of measurement
	Lowest detection value
	Measuring error

	1）
	H2
	1 ～ 10000 µ l/l
	1µ l/l
	±10%

	2）
	CO、 CO2
	5～  50000 µ l/l  
	5µ l/l
	±10%

	3）
	CH4
	0.1 ～ 20000 µ l/l
	0.1-0.5 µ l/l
	±10%

	4）
	C2H4
	0.1 ～ 20000µ l/l   
	0.1-0.5 µ l/l
	±10%

	5）
	C2H6
	0.1 ～ 20000 µ l/l  
	0.1 -0.5µ l/l
	±10%

	6）
	C2H2
	0.1 ～ 5000 µ l/l  
	0.1-0.5 µ l/l
	±10%

	7）
	H2O（optional）
	1 ～ 800 µ l/l
	1µ l/l
	    ±10%

	8）
	Total hydrocarbon
	1 ～ 8000 µ l/l

	9）
	Total air content
	0.2 ～ 15%

	14
	Stability（measured deviation）
	Under the same test condition, the deviation of test result shall be no more than 10%（medium concentration）

	15
	Electrostatic discharge immunity
	Grade 4，± 8kV－± 15kV

	16
	Electrical fast transient immunity
	Grade 4，± 4kV

	17
	Surge (shock) immunity 
	Grade 4，± 4kV

	18
	Earthquake resistance ability：seismic wave is sine wave. Time of duration: three circle wave. Safety factor:1.67
	Area with grade 9 seismic intensity：

Ground horizontal acceleration 0.4g, ground vertical acceleration 0.2g

	
	
	Area with grade 8 seismic intensity：

Ground horizontal acceleration 0.25g, ground vertical acceleration 0.125g

	
	
	Area with grade 7 seismic intensity：
Ground horizontal acceleration 0.2g, ground vertical acceleration 0.1g

	19
	The temperature of storage and transportation under extreme environment 
	-40 ℃ ～＋ 80 ℃

	20
	Protective property of the enclosure
	Outdoor installation parts (the system and communication control unit） IP56

	21
	Boundary dimension
	width 585mm × depth425mm × height 1010mm

	22
	Total weight
	125kg

	23
	Basic size 
	width 700mm ×depth 380mm × height300mm


Preparations before installing the hardware of on-line monitoring system of transformer oil chromatography
Choose appropriate oil extraction port and oil return port
The on-line monitoring system would firstly extract oil from the transformer, analyze the oil, and then send it back to the transformer. Therefore, it is very significant to choose the oil extraction port and the oil return port for the accurate analysis of dissolved gas in oil. In order to select appropriate oil extraction port and oil return port, it usually includes the following content:

Confirm the location of oil extraction port and return port
We suggest that extract the oil from the bottom of the transformer, return from the upper part of the transformer. The oil in oil extraction port shall be able to fully represent the oil in the transformer, as shown in Pic 3.1. 
[image: image2.png]L33 ]
]

Transformer
oil tank

valve 2

Iterface
D2

e
E]i

interface valve 1

B oL

=

Stainless steel pipe (Oil
return pipe)

OITEHE (EHE)

/o KEARNE

Oil flow direction
LS L]

Transformer online

monitoring system

AEERERSAINER

o o o
D

i

i

WHFH
Oil flow direction

[T hass

Cement base

N O3F4E (BiE) Stainless steel pipe

KEAFNL

(oil inlet pipe)





Pic 3.1 Connection diagram of oil system
	[image: image3.png]


Note
1. It is not recommended to treat the valve in the cooling duct or pressure pipeline as oil extraction (return) port. 

2. It is not recommended to share a valve for oil extraction port and oil return port. 


Confirm the specification parameter of oil extraction port and oil return port
Check the type of oil extraction port, oil return port and connecting valve, other important parameter like thread specification of connecting valve as well as valve height. Estimate the distance between chromatographic data acquisition unit and oil extraction (return) port properly so that the manufacturer could produce corresponding switch valve and oil tube with enough length.  
Determination for installation location of field monitoring host

When choose the installation place of field monitoring host, the following aspects shall be taken into consideration. 
When select the installation place of field monitoring host, we prefer the spot which is convenient for transformer maintenance and remain a certain distance from other equipment.  
②A space of 1.0 meters should be reserved on both sides of the field monitoring host (front and back) for its installation and maintenance. The front side (with indicator light) should face to inspection channels.

The installation position of field monitoring host should be close to the oil extraction/return port. After the installation position of field monitoring host is determined, we could correctly estimate the distance from the installation position to the oil extraction/return port. 
The position shall be near to the oil extraction (return) port.
An AC220V power supply shall be nearby. 
The construction of basis platform 
As shown in Pic. 3,2, install the basis platform in accordance with the requirements of picture below. 

[image: image4.png]4-M12*100 Expansion bolt

Ground galvanized iron bar

Ground this end

| Connect to the transformer oil outiet 950 Galvanized pipe

Connect to the
cable trench Connect o the transformer return port

Base construction instructions

1. When fixing the expansion bolts, the exposed

surface is about 25mm

2. Pre-embedded 3 pieces of 50 galvanized pipes

3. The oil inlet and outlet pipes respectively pass

through the oil outlet and return interface valve of the

transformer through the pipe B and pipe C

4. The power line and communication line are

connected to the cable trench by pipe A

5.A, B, C pipe extension direction may be opposite

6.After the expansion bolts and the base platform
Ground galvanized ion bar @re completed, install the grounded galvanized iron

v bar, which can be higher than the thickness of the

base plane iron bar

7.Since the chassis is opened front and rear, there

must be a 1 meter operating space before and after

the base





Pic 3.2 Schematic diagram of basis platform
Choose power supply for field monitoring host
The on-line monitoring system uses AC 220V power supply, less than 1000W power dissipation. Before installation, the operator shall measure the distance between the control cabinet of power supply and field monitoring host.
3.4 Choose the location for installing data processing server (computer) 
It is recommended to install the data processing server in the master control room of transformer substation or electric control room of power plant (reserved AC 220V power supply and channel of telecommunication cables). The appearance of data processing server shall meet the standard of 19 "industrial case, which can be installed in the reserved space of the 19" standard industrial control panel. If there’s no spared one, you need to install an additional 19 "standard industrial control panel which needs to purchase later. 

	[image: image5.png]


Note
We suggest using the power supply for transformer overhaul as the supply for field monitoring host.  


3.6 User’s Information 
Please provide the following information, including the table of user’s basic information and transformer’s basic information. It is helpful for the future services and accurate processing in time when the problem occurs. 
	Company name
	
	Address
	

	Factory name
	
	Address
	

	Project leader
	
	Mobile
	
	Fax
	

	Installation personnel
	
	Mobile
	
	Fax
	

	Operating maintenance personnel
	
	Mobile
	
	Fax
	

	Transformer manufacturer
	
	Module
	

	Ex-factory time
	
	Commissioning time


	

	Picture of transformer
	
	Voltage classes
	

	Transformer capacity
	
	Type of cooling
	

	Total weight of oil
	
	Type of oil
	

	Maintenance record of transformers 

	Maintenance date 
	
	Cause
	

	Content
	
	Result
	

	Analyze data of the gas dissolved in oil for the transformer 

	Highest air temperature around the year
	
	Lowest air temperature around the year
	

	Relative humidity 
	
	Altitude 
	


The hardware installation of online monitoring system of transformer oil chromatography

The on-line monitoring system is a high-integrated instrument. So the user would be better not to dismounting it whether under the warranty or not to avoid unnecessary troubles. Before installation, the operators must read and understand all the contents of this section, which is very important to finish the installation smoothly.

Required equipment: 
Field monitoring host：overall dimension： 600 （width） × 1100 （height） × 520 （depth） mm ；
Installation procedure 
Cable laying 
Laying communication cables/ optical cables 
The data processing server of the on-line monitoring system is installed in the master control room while the field monitoring host is installed at the scene of the transformer. When using cables for data transmission, they can communicate with each other through the Ethernet. So we need to lay a 4-core multimode optical cable or unshielded twisted pair (if required). The length shall be in accordance with actual distance.
Laying power cables
The field monitoring host of the system uses 220V AC power supply. A 3×1.5mm2 armored power cable shall be laid between the power supply panel on site and the room of field monitor host. 
Laying ground wire
In order to guarantee that the field monitoring host could be effective grounded, there shall be a ground wire connecting field monitoring host cabinet and effective earth point. The grounding cable uses copper stranded wire pressured on both ends with tinned copper. The sectional area is no less than 4 mm2; we use a piece of flat steel with 48 mm cross-section and 4 mm thickness as the grounding conductor.

The installation of oil extraction pipe and oil return pipe
The flowing direction of oil extraction/return pipe
According to the location and direction of oil extraction/return valve, determine the flowing direction of oil extraction/return pipe in line of on the principle of short distance and beauty. 

	[image: image6.png]


Note
once the direction of oil extraction/return pipe is determined, in order to avoid the pipe suspending in the air, we suggest fasten the stainless steel pipe when entering or leaving the protection tube. 


Laying the protection tube
Along with the direction of oil extraction/return pipe, spare room for a channel of φ50mm protection tube in the oil pool at internal bottom of transformer, then pave the protection tube required. 
	[image: image7.png]


Note
We suggest usingφ50mm galvanized steel pipe as protection pipe with the protection of a stainless steel casing inside. There’s a distance of 1000mm right angle extension near the transformer. 


The installation of oil extraction/return valve
Before installing the oil extraction/return valve, firstly unscrew the nut and replace it with a new oil-resistant seal ring. According to the method of drawing oil samples, receive the waste oil with a empty bucket or other containers. Then unscrew the nozzle, let the sample oil flow from the nozzle. Regulate it to moderate flow, then screw the valve rapidly until the seal ring is pressed tightly and solidly. The picture of valve is as follows.  
[image: image8.jpg]


Oil pipe laying
⑴ 、 The oil pipe is wrapped in a foam thermos pipe. 
⑵ 、 Enclosed with thermal insulation pipe, the oil pipe shall thread through the protection tube. Lay the oil pipe in the direction of pre-laid protection tube.
Oil pipe connection 
Connect the reserved interface in the oil extraction/return valve with the laid oil pipe. 
Charge and discharge the oil, connecting the oil extraction/return pipe with the equipment 

In order to prevent any foreign body falling into the oil pipe when it is coating foam thermal insulation pipe, we shall back and forth charge and discharge oil for oil extraction/return pipe.

1 、Unscrew the oil drain bolt at the side of connecting valve anti-clockwise.
2 、When the sample oil free from bubbles flows from the oil pipe rapidly, the oil pipe of chromatographic data acquisition unit shall receive the oil immediately. 
Leakage detection after installation 
After finishing the installation of oil extraction/return pipe in the transformer and monitoring equipment and oil pipe butt, check all the junction points of oil pipe if there’s any leakage by observing. 
⑴ 、 Use cloth or tissue to clean all the connecting points of transformers and equipment. 
⑵ 、 After one hour observation, if there’s no oil stains in the junction point, then we assume there’s no leaking. 
	[image: image9.jpg]


Warning 
No foreign body would be allowed to enter into the transformer during the installation of transformer valves. 


	[image: image10.png]


Note
The oil pipes supplied have been through thorough cleaning in different ways. Since it doesn’t generate any pollution for the oil of transformers, it must meet the requirements of practical application. 


	[image: image11.png]


Note
When connecting the oil circuit, try to avoid the use of fittings. Screw the connectors with the seal rings like valves tightly in case of any leakage. 


Electrical Connection 

Check the connection of power cables 

The power cable of field host is a armoured power wire in a length of 3×1.5mm2. Connect AC 220V power supply with the upper terminals of power switch in the panel of field monitoring host. An overhaul is imperative after connection to confirm there’s no misconnection. 
	[image: image12.jpg]


Warning
Before connecting with the power cable, we shall firstly confirm that the cable is not charged, the power switch of cabinet is in OFF state, so as to ensure the safety of the installation operators and equipment. Otherwise, it may lead to serious or fatal harm to the equipment and installation operators. 


Ground Wire Connection
The ground wire could connect the field monitoring host and effective earthing point by bolt. 

 Communication Cable Connection 
According to the drawings, connect the communication cables with the corresponding communication connectors. 
	[image: image13.png]


Note
Make sure the internet access of field monitoring host and the communication interface of server are fixed tightly before connection. 


4.2.3.7 Power up the system 
After the confirmation of correct electric connection without any mistake, the data processing server and field monitoring host would separately plug into 220V AC power supply. 
Once powering up, the operator shall carefully observe if there’s any abnormality happened. The power light in the control panel of chromatographic data acquisition unit shall be in normal indication. 

Notes for the operation and maintenance

Reminding for the operators and maintenance personnel
Daily Inspection
⑴ 、 Related personnel shall conduct regular inspection. Check the data with the method of sampling at certain intervals. 
⑵ 、Check if the system is running properly before power switch. 
⑶ 、Check the leakproofness of gas circuit and oil circuit 
⑷ 、Check if the valve of oil in/out port is normally open. 
Check the valves of oil in/out
⑴ 、 When the system has been put into operation, the valves of oil in/out in the transformers shall be always open. 
⑵ 、 If the operators discover any oil leakage or fracture in the oil pipe, please close the two valves in the transformers in time and then cut the power supply of data acquisition unit. Then the operator shall inform the engineer in charge as soon as possible.

The instruction for indicator lights and instrument of field monitoring host
Green indicator light： There is a green indicator light in the control board of field monitoring host. If it is on, it means the data acquisition unit is running. 
Red indicator light： There is a red light in the control board of field monitoring host, indicating the status of power supply. If it is on, it means the field monitoring host is powered up. 
Yellow indicator light： There is a yellow alarming light in the control board of field monitoring host. If it is on, it gives an alarm for the data acquisition unit. The specific alarming reason could be found from data processing server. The operator shall manually reset the power supply of field monitoring host for emergency handling. If it is still in the alarming state, then please ask the responsible engineers or technician of manufacture for help. 


[image: image15.png]R e e N Huazheng



[image: image16.png]R e e N Huazheng



[image: image17.png]