
HZCF-400 

Battery Load Bank

USER MANUAL
Huazheng Electric Manufacturing(Baoding) Co.,Ltd

Content

1PART I GENERAL


3PART II Junction port and connection directions


5Part III Operation Directions


13PART IV PC Software Operation Directions





PART I GENERAL

1.1
 General Introduction

Battery Load Bank is a special instrument for the test of NiCD and Lead-acid storage battery string of the whole string voltage of 24V, 48V, 110V, 220V, and it adopts current advanced testing technology theory, and has obtained a series of breakthrough in research and application of new technology, new parts, new material and new techniques, which is designed in accordance with the requests of national related testing and maintenance regulations and it is a special detection instrument for the performance detection of stationary battery. Its big discharge power, small volume, light weight, complete function of data management software of upper computer could greatly reduce the work load of daily testing and maintenance of stationary battery.
1.2 Main Functions and Features 

The product is utilized color touch screen. It can be operated via finger or the touch pen with convenience and flexibility.
Data save mode: Internal save and external save(SD Card )
Enhanced over voltage protecting function , 

Automatically recovery the over current protecting function 

Overheating protection .

Discharge Function: 

Perform discharge of constant current taking advantage of intellectualized dummy load after the battery string is removed from system, set up the parameters of “discharge current”、“discharge time ”、“discharge capacity” 、“final protective voltage of whole string” and “final protective voltage of cell”, and the tester could carry out discharge function automatically, display discharge current、battery discharged capacity、the whole string voltage, cell voltage, discharge time and etc at real time; when the string reaches setup value of final discharge voltage、setup value of final discharge capacity、setup value of final discharge time、any cell voltage is below setup value of final cell voltage or manual final operation could stop discharge test.
It could save 10 groups of discharge test data; the user could perform query, deletion, and export operation of SD card. 

 The computer could connect with instrument via the serial, perform test control and real-time monitor of instrument, and carry out graphic analysis. 

The computer could connect with instrument via the serial, perform test control and real-time monitor of instrument, and carry out graphic analysis.
Automatic protection function: 
The tester would stop the test automatically when it could detect the abnormity of the whole battery string or cell, and the working abnormity of tester in order to make protection of battery during the test process. 

 The host machine of tester adopts the design integrating the monitoring part with power part, the power part adopts new-type high-effective parts, and it is a storage battery comprehensive tester with small volume and high efficiency. 

 Humanized operation interface, simple operation, clear flow, and each operation could have English cue. Aquamarine blue high-brightness, large-screen LCD, and the display effect are clear and beautiful. 

 Powerful functions of upper computer data management software, friendly interface, which could offer data management, print, analysis, statistics of report forms, automatic creation of test report , etc 

1.3Test Procedure Introduction:

Discharge Test Procedure: 
Step1: Pull“ On” on the discharge switch ( to prevent reverse connection of the discharge cable and damage the tester , and also if misconnection, the warning will be given.)

Step2: Connect the discharge cable to the the host machine and battery bank respectively. ) Note: Red line is + positive ; Black line : - Negative ) reverse connection will be warning . ( See details in section 2.5 )
Step 3: Connect group voltage test line to the two poles of battery string.

Step 4: Plug in and switch on the tester.

Step 5 : Enter into discharge test parameters setup.( see details in 3.2) 

Step 6: Pull “ off”on the discharge switch . 

Step 7: Press “ ok” start test 

PART II Junction port and connection directions
2.1Junction port introduction 

[image: image47.png]o7

Test Template




[image: image1.jpg]



[image: image45.png]uazheng
HUAZHENG ELECTRIC MANUFACTURING (BAODING) C0.,LTD




[image: image46.png]


[image: image2.png]) i

Test Setup Test Template

@ s

Data Mgmt System Mgmt




Data management             System management
2.3 Keys: (Touch screen and keys) 

[image: image3.png]eil\lnve Forward

(E——Move Backward
(E)—ok




2.4 The host machine Wiring directions

2.4.1 Connection and disconnection rules

Before test, wiring is in accordance with firstly connecting the tester, and then connecting the batteries. 

After finishing test, user should disconnect the lines on the battery string, then the lines of the tester.

2.42 Wiring of Discharge cable 

Connect “+”(red) with positive pole of a string of battery, and connect“-”(black) with negative pole of battery string. Prohibit to connecting contrarily!
2.4.3 Wiring of string voltage collection lines 

Connect string voltage lines to the corresponding poles of the battery string, Connect “+”(red) with positive pole of a string of battery, and connect“-”(black) with negative pole of battery sting. Prohibit to connecting contrarily!
2.4.4 Connect with 220V power cord of tester. The user should carefully View the wiring is right or not, and notice the positive and negative wiring of battery terminal and the terminal of voltage collection line are right or not, it is prohibited to connect contrarily! 
2.4.5 Connect with power supply, and the tester could run after View.
Part III Operation Directions

3.1 Discharge Function 

Perform discharge of constant current taking advantage of intellectualized dummy load after the battery string is removed from system. when the string reaches setup value of final discharge voltage、setup value of final discharge capacity、setup value of final discharge time  could stop discharge test
3.1.1 Test preparation 

Firstly connecting discharge cable to the tester, then to the batteries. it adopts in parallel connection between battery string and the tester . 

3.1.2 Parameters setup

  Turn on the tester and enter into the interface below , choose “[image: image4.png]Test Setup



” — “[image: image5.png]Discharge



”, enter into interface of discharge parameters 
[image: image6.png]RoomNo 0001 StringNo 01 StringNum 1
StringType CellType 8 = CellNum B =
NominalCap 100Ah CellOrder 8 = Dis.Method| Const-I

Dis.H.R 10h I-Descarga| 10.0A

Condic.Fin.Prueba
WMinString 43.20V UMinCell g =
CellTotal - - CellVolt. B E
C-Discharge 100Ah T-Discharge 10:00(H:M)
Ok e ESC

Prompt:The touch screen. please click.




 Figure 3.1.2 Interface of setup of discharge parameters 

Input parameters setup according to the prompt of the interface, if setup error,“ Flute. Flute, flute. "will be warned .
Room No. 0001-9999

No of battery string 01-99

Number of Battery String: 1-2string

StringType:Type of String Voltage,according to the type of string voltage you need to test, for example, 24V or 48V etc…

Cell Type: The current parameter does not need to be set

CellNum: The current parameter does not need to be set

NominalCap:Rated Capacity,Rated capacity of individual battery

Cellorder: The current parameter does not need to be setTest time: 

Dis.Method:Mode of Discharge

Constant current: Value of current setup should not bigger than rated current.

Constant Power: 48V: Max value of power setup =(Type of string *1.2* Max discharge current/1000) KW

Dis.H.R:Discharge hour rate,0.5-10H optional 
I-Descarga: Discharge current or power setting
UMinString: Set voltage lower limit,during discharging to battery, if don’t need monitor string voltage , user need setup value of string voltage as “0” in terminal condition .
UMinCell: The current parameter does not need to be set
CellTotal: The current parameter does not need to be set
CellVolt: The current parameter does not need to be set
C- Discharge: Set discharge capacity
T- Discharge:Test time: Hour: Minute; Min 1min, Max: 99h59min.

After finishing setup and confirm the connection line again, Close the discharge switch and begin to discharge 

[image: image7.png]RoomNo 0001 StringNo 01 StringNum
StringType 48V CellType CellNum 8 =
NominalCap 1 thod| Const—I

Dis-H.R Use external storage card, Y [3r82 8008

es to start the Discharge?

UMinString] ==
CellTotal . Yes . No A =
C-Discharge 100Ah T-Discharge 10:00(H:M)
Ok e ESC

Prompt:The touch screen. please click.




Figure 3.1.2-1 Interface of discharge 

Click”Yes”, start discharge 
3.1.3 Interface of Test

[image: image8.png]Discharging -

Terminate Condition
WMinString UMinCell C-Dis—Set T-Dis—Set
43.20V - 100Ah 10:00 (H:M)
StringVolt 48.30V I-Discharge 80.0A
C-Discharge 1.5Ah T-Discharge 0:01 (H:M)
WMaxCell-1 - UMinCell-1 =
WMaxCell-2 - UMinCell-2 —

Prompt :




                                   Figure 3.1.3 Interface of Discharging
If happen to warning for the data, it display “ Red” 

View setup information: user can modify warning condition on test.

Mute: If reach warning condition, the tester will display reason of warning and give off prompt tone “Flute. Flute, flute… 
EQUIT : Stop monitoring。
3.1.4 Stop of discharge:

below setup value of final cell voltage or manual final operation could stop discharge test, the tester proceed heat dissipation before turning off power supply of tester so as to prevent the damage of the tester .
[image: image9.png]Manual

Terminate Condition

WMinString UMinCell C-Dis—Set T-Dis—Set
43.20V = 100Ah 10:00 (H:M)
StringVolt 48.30V I-Discharge 80.0A
C-Discharge 1.7Ah T-Discharge 0:01 (H:M)
WMaxCell-1 - UMinCell-1 -
WMaxCell-2 - UMinCell-2 —
View Settings| .. Mute | . ESC

Prompt:The discharge stop




Figure 3.1.4 end of discharge

End of test: View the test data and see in3.3
Turn off discharge switch and power supply of the tester and disconnect connection lines , firstly disconnecting connection line on the battery, then on the tester . 
3.2 Test template function

Main interface enter into
Each function of the tester can supply 10groups of template of test parameters, self-defined parameters. 
3.3Data management function

Data save mode: internal save and external save

Main interface enter into” [image: image10.png]Data Memt



”, click the icon of discharge test.
3.3.1Mode of Data save: 

To use internal save mode, the time interval for one minute during the test. The tester automatically allocate the save time according to the test time.

Max 10groups test data for internal save 

[image: image11.png]2015 17 00

01 2015-10-29 14:10 0001 0001

| Export Exp-All Del  Del-All, View ., ESC |










                Figure 3.3.1 Data internal save

“Export”: Export of Data to choose one record, then click”Export”to SD Card .

“Exp-All”: Export all the data: to click “ Exp all”to SD card .

Del-All : Delete all the data 

Del: delete one record

View: View information: firstly choose one record and click “ view information” for detailed data information 
3.3.2External Save (SD card) mode: 

Use external save, time interval of data save can be setup, Min data save time for 5s.

External save: Max 999groups test data

File name: Function code-Room No.-Battery string No.-battery No.-Date & Time 

F: Discharge data: F0001-01-150112135048.CFJ

[image: image12.png]2015 10 00

NO. file name
1 F0001-01-151018093220.CFJ





Figure3.3.2 Discharge test data

Each page displays 9 records , to View through page up and page down

Del-All :Delete all the data 

Del: delete one record

View: firstly choose one record and click “view” for detailed data information.

3.3.3 View information

[image: image13.png]Manual

Alarm-condition

WMinString UMinCell C-Dis—Set T-Discharge
43.2V - 100.0Ah 10:00 (H:M)
U-String 48.30V I-Descarga 80.3A
C-Discharge 1.6Ah T-Dis—Set 0:01 (H:M)
WMaxCell-1 - UMinCell-2 =
WMaxCell-2 - UMinCell-2 —
TrendPicture | . ESC

Prompt:The touch screen. please click.




                          Figure3.3.3 End of test

Graphs can’t be Viewed if test time lower than 1min, 

TrendPicture:Graphs of data,View string voltage.

3.3.4 Graphs of data 
[image: image14.png]Group Voltage Type: |U-String

52. 94V
Max:  52.84V
Min:  46.48V
SPace:1m Os
StringNum:1

CellNum:24

1.093v

Hdiv

46. 38V,

0:00:00

4:56:00 Time

U-Group D-Group UpPage DownPage Narrow Amplify  CLS = ESC
Prompt:The touch screen please click.




Figure 3.3.4Graphic of string voltage

View data fixed in time, click graphics field, the time and voltage will be displayed.

3.4 Date & Time setup

 Enter into “[image: image15.png][ B

Svstem Memt



—[image: image16.png]@

Date&Time



”the interface of time setup

[image: image17.png]10-18-2015 10 02









Figure 3.4 Interface of Data& Time setup
After finishing setup, to click”confirm”and come into effect

3.5 Calibration of Touch screen 

Enter into “[image: image18.png][ B

Svstem Memt



—[image: image19.png]g

TP Calculate



”interface of calibration

[image: image20.png]Date&Til Setup

o) [

PRMCalculate About ESC







     Figure3.5 Calibration of Touch screen

To click”Yes” and begin calibrating

3.6 Restore factory settings 

  Enter into“[image: image21.png][ B

Svstem Memt



—[image: image22.png]PRM Setup



—[image: image23.png])

FactoryReset



”the interface of factory default
[image: image24.png]2015 10 04

CellMaint]
SystemSet ESC




Figure3.6Restore factory settings

3.7 Setup of data save 


Data save: internal save and external save (SD Card). To choose external save (SD Card), save interval: Min 5s for one time. internal save: the tester automatically setup according to test time.

Enter into “[image: image25.png][ B

Svstem Memt



—[image: image26.png]PRM Setup



—[image: image27.png]SystemSet



” the interface 
[image: image28.png]stemConf.

MaximumVoltage: 456.0V
Overcurrent: 1
Storagel.ocation:
StoragelInterval: Store-In
COM-mode: SD Storage
Cell-NUM: 24
L SAVE

Prompt:The touch screen. please click.





Figure3.7 data save setup

3.8 Time Save Setup

Enter into “[image: image29.png][ B

Svstem Memt



—[image: image30.png]PRM Setup



—[image: image31.png]SystemSet



” the interface 

[image: image32.png]stemConf.

MaximumVoltage: 456.0V
Overcurrent: 1
Storagel.ocation: SD Storage

StorageInterval: 5 sec
COM-mode: Wireless
Cell-NUM: 24

L SAVE

Prompt:The touch screen. please click.





Figure 3.8 Interface of time save setup

3.9 Parameters calibration 


Use under the guidance of manufacturers!

Enter into “[image: image33.png][ B

Svstem Memt



” — “[image: image34.png]@7

PRMCalculate



”the interface of calibration.

[image: image35.png]



Figure 3.9 Interface of parameters calibration
     。Parameters have been calibrated out of factory. 

3.10About Product

  Enter into” [image: image36.png][ B

Svstem Memt



” — “[image: image37.png]About



” the interface 
[image: image38.png]2015 10 07

About Interface

VoltageType: 220V 110V 48V 24V
Nominal-C: 70A 150A 150A 150A
CS-Type:
Versionlnfo: V4.0
StoreMode: Store-In
ESC__




Figure3.10 Interface of product information

Type of Voltage: Rated voltage of current sting voltage 

Rated current: Max current of corresponding to different voltage 

Communication mode: mode of communication for the host machine and cell voltage monitoring module.

Save mode: Internal save and external save

PART IV PC Software Operation Directions

Chapter 1 General

4.1 Application

This software is data management software for stationary battery comprehensive tester.

4.1.1 System configuration

The lowest configuration request for the computer to use this software:

All kinds of desktop computer and laptop computer with PENTIUM of standard serial、USB interface or 100% compatibility.

One CD-ROM used for install the file.

One HDD(for example :C:),at least 80M useable disc space

EMS memory over 64M.

Display resolution over 1024*768.

WINDOW 2000\NT\ME\XP\2003 operation system.

4.1.2 Setup

Click setup software SETUP .exe, carry out operation in light of interface prompt, and the user could finish the setup of data.

4.1.3 Startup

Run “desktop-icon” or run “start-program-icon” to enter into main menu. 

4.2 Operation-file

[image: image39.png]_@u: Powercell Battery Analyzer

Tools(T)  window(\Ww) HelpiH)
5 open(0) Chrl+0

Expork

i Exitix)





4.2.1 Open

Select ”File-Open” in the menu to enter into test file interface, select one or several  test files, click open, and the selected test file would be opened.

[image: image40.png]My Recent
Documents

My Docurents

My Network

[SE3]

[Scovot-or-torzsniszne
[5)covot-or-10tosess7zz
[ covot-or-t10r0100159
[5)covot-or-10rosssets
[ covot-o1- 110105055400
[S)covot-or-t10tost 12210
[ ——
[Sjronot-or-1ot0s09ss29

[Sjronot-or-tiot0s100757
[Sjronot-or-tiotosoess
[S)wooro1-110104155058
3 wsoro1-t10to4is3z21
3 wsoro1-t10105082711

File name:

Files of type:

2R





4.3 Data operation

discharge test could view test data, test pattern, cell contrast, maintenance solution.

Test data

[image: image41.png]8 Room: 00001 (J0001-01-110104153058.CFJ)

‘Test Inforation | Test Chart | Cell Constrast | Solution

foonptty
Tmed oo

| i - wock_00n

RoomName 00001 - oos 228

Pacte o1

e

compe v

Cnormal 1008k
Timei 00100

PackNum 1 -
Upack #9637 Ipack 004
CeliNu 2

cap. 0081 Ubus 55937
Cconnect  From-
5 1Pack
U2 2068 2071 20600 2067 2066
U324 20m 2074 2068 20 2077

2071 2060 2067 2066
20742068 20 2077

Monitor Parans
SetTime OHMin
Upackuplimit 56 507





Test pattern

[image: image42.png]8 Room: 00001(F0001-01-101231095158.CFJ)

Test Infomation | Test Chit | CellConstas | Soltion

T 5000V
4900
4z00v
4700
4500V - = =

00000 G700 01400 02100 02800 B3SO0 04200 G400 DSG0D 10300 11000 147.00 12400 13100 1:3600 1:4500 1:5200

Iiischarge
10008

so0a |

00a
00000 G700 01400 02100 02800 BI500 04200 G400 DSG0D 10300 11000 147.00 12400 13100 1:3600 1:4500 1:5200

Cag250.08h §
20002h
150.08h
10008k |
s008n
008h

00000 007.00 01400 021:00 02800 0:3500 04200 04300 05600 10300 1000 117.00 12600 1:31:00 1:3300 14500 15200

U 2000V
1.500v
1.000v
0500
0000y

19 12 13 14 15 18 17 15 19 140 101 142 113 114 14§ 108 107 118 148 120 121 1-22 123 124

450
400
00000 007.00 01400 02100 02800 03500 4200 04300 C:S600 1:0300 11000 11700 1:2400 1:31:00 1:3300 14500 1:5200





Maintenance solution

[image: image43.png]8 Room: 00001 (F0001-01-101231095158.CFJ)





4.4 Generating Report
Click print under maintenances solution window, pop up report parameter dialog box, fill in parameters, if needs to create process data, select process parameters and interval of sampling, and the created  report would include process data.

[image: image44.png]Parameters

©FRepart OFem

Cellnto Repantlnfo

CelMol IistallDate ¥| oot [o0001

Fastory i

Techuics Reporter
Pack Chant
ClUpsck Cliowck [JCan  CICelU Contiast [0bus

(el Cuve B0 (Mo ) - [ Contrest Curv(<=12)

Ot 0s on () 0s Ou
02 O Ot 02 O Ot
03 Ou O 03 Ou O
e O O D4 O O
Os O [WE Os O [WE
Os O1s Oz O O1s Oz
07 O 05 o7 O 05
Os Ot =] O Ot [mE]

Data O





Statement

Our company could improve and complete the technical performance of stationary battery comprehensive tester timely. Simultaneously, this manual could improve with upgrading of products; some part of content could change. If it is changeable, no additional notice.

The full technology of stationary battery comprehensive tester is exclusively owned by Foresight Electronics Technology Co.,Ltd., any individual or unit could not have rights to change. The aim we offer this product is to help the customer complete the detection and maintenance of stationary battery comprehensive tester. If it is used illegally, our company would claim the legal responsibilities.


