[image: image7.png]R e e N Huazheng




[image: image13.png]220 V 50Hz

NN
QF

KM

CT-50/5A

T(S)D

18

2

51

2

KA

100(5OKV/100V






HZQ Gas Type Testing Transformer
USER MANUAL
Huazheng Electric Manufacturing(Baoding) Co.,Ltd
Contents
1HZQ Gas Type Testing Transformer


1I、Introduction


1II、Structure


1III、Principle of Work


2IV、Technical Parameters


7HZXC HV Hipot Control Unit


9HZTC HV Hipot Control Unit


9I、Outline


9II、Main Characteristics


10III、Panel introduction


11IV、Technical Parameter


11V、Connection Wire Sketch drawing of It and High Voltage Test Transformer


12VI、Manual Explanation


12VII、Usage and Maintenance


13VIII、Supplementary Explanation


14IX、Electrical schematic diagram




HZQ Gas Type Testing Transformer
I、Introduction

The Test Transformer calls the booster, it is the basic test equipment used by the power station, supplying and distributing the electrical power system and the scientific research unit. Which used in the insulated intension test on all kinds of electrical products, electrical equipments and insulated materials, testing the insulated level of products, discovering the insulated objection of quizzee, scaling the capacity burdened voltage. 

II、Structure
They make up of the high quality cold rolling　silicon steel piece by HZQ alternating current test transformer, HZQ-JZ alternating and direct current amphibious light high voltage test transformer. The winding is the　concentric pagoda  and multilayer cylindrical type, low-voltage　winding in inner, high-voltage winding in outside; Outer cover is portable which has characteristics, such as volume smallness, weight light, the shape prettiness and move convenience and so on.

III、Principle of Work
Connecting the control unit (it is the supplementary equipment of test transformer, detailed see the explaining book) with work frequency 230V (above 10KVA with 400V), adjusting 0-230V/400V voltage input to HZQ (HZQ-JZ) test transformer primary winding through autotransformer. According to the principle of electromagnetic influence, the secondary (high voltage) winding may gain the same multiple voltage value than the primary winding with the circle rated that is the high frequency voltage of work frequency. It can obtain the direct current high frequency voltage after commuted by high frequency voltage silicon stack and filtrated by capacitor, among whose amplitude value is the 2 times value of work frequency.

This series product divides into three kinds: the alternating current is named HZQ, the alternating and direct current is named as HZQ-JZ, meanwhile, may connecting HZQ, HZQ-JZ with 230V switch to form series excitation transformer.
IV、Technical Parameters
1．Technical parameters of HZYQ series alternating current test transformers

	Model
	Capacity（KVA）
	High Frequency Voltage

Output Voltage

（KV）
	High Frequency

Voltage

Output

Current（mA)
	Low Frequency Voltage input
	Ratio
	Tempera- ture(℃)

raised/

30 minute

	
	
	AC
	DC
	AC
	DC
	V
	A
	
	

	HZQ-1.5
	1.5
	50
	70
	30
	15
	200
	7.5
	500
	10

	HZQ -3
	3
	50
	70
	60
	15
	200
	15
	500
	10

	HZQ -5
	5
	50
	70
	100
	15
	200
	25
	500
	10

	HZQ -10
	10
	50
	70
	200
	100
	200/400
	50/26
	500
	10

	HZQ -20
	20
	50
	70
	400
	100
	400
	53
	500
	10

	HZQ-30
	30
	50
	70
	600
	100
	400
	79
	500
	10

	HZQ -40
	40
	50
	70
	800
	100
	400
	105
	500
	10

	HZQ -50
	50
	50
	70
	1000
	100
	400
	132
	500
	10

	HZQ-5
	5
	100
	140
	50
	50
	200
	25
	1000
	10

	HZQ -10
	10
	100
	140
	100
	100
	200/400
	50/26
	1000
	10

	HZQ -15
	15
	100
	140
	150
	100
	400
	37.5
	1000
	10

	HZQ -20
	20
	100
	140
	200
	100
	400
	53
	1000
	10

	HZQ -30
	30
	100
	140
	300
	100
	400
	79
	1000
	10

	HZQ-40
	40
	100
	140
	400
	100
	400
	105
	1000
	10

	HZQ-50
	50
	100
	140
	500
	100
	400
	132
	1000
	10

	HZQ -10
	10
	150
	210
	67
	100
	200
	50
	1500
	10

	HZQ -10
	10
	200
	
	50
	100
	200/400
	50/25
	2000
	10

	HZQ -15
	15
	150
	210
	100
	100
	400
	37.5
	1500
	10

	HZQ -20
	20
	150
	210
	133
	100
	400
	50
	1500
	10

	HZQ-20
	20
	200
	280
	100
	50
	400
	50
	2000
	10

	HZQ -30
	30
	150
	210
	200
	100
	400
	75
	1500
	10

	HZQ -50
	50
	150
	210
	333
	100
	400
	125
	1500
	10

	HZQ-50
	50
	250
	
	200
	
	400
	125
	2500
	10

	HZQ-150
	150
	150
	210
	1000
	100
	400
	375
	1500
	10


Note: 100KVA and the above input voltage may enhance to 3000V or　proposed by the users.

V、Test Wiring

Wiring schematic drawing of the alternating current (work frequency) pressure test.

[image: image8.png]Huazheng




Explanation:

Carrying through the alternating current pressure test, it does not only use the HZQ test transformer, but also the HZQ-JZ test transformer. But, when performing the alternating current pressure test, don’t pull out the short circuit pole on the high compression leg.

2. Wiring schematic drawing of direct current leak and direct current pressure test.　

[image: image1.png]



Explanation:

2.1. Engage in the direct current leak and direct current pressure test, it should only use the HZQ-JZ test transformer and pull out the short circuit pole worked on the high compression leg.

2.2 When do the electric cable pressure, not to combination capacitance in stead of potentiometer，it should read value of the high pressure voltage exactly and it is very intuitionistic.

2.3 When the direct current is leaked, the microampere meter may direct readout the value of the direct current pressure test.

2.4 Complete the direct current leak, may carry out direct current pressure test directly without taking out stitches.

2.5 Need to add capacitance when doing arrester test.

3. Series Excitation Combination Test Transformer Wiring.

3.1 When carry out alternating current series high frequency voltage test transformer, may form test transformer with high voltage compounding a few set of HZQ . This principal is that HZQ  high frequency voltage winding is connected with the excitation wilding, and make their parameter the same with the next-step primary winding.

3.2 Schematic drawing of two set of HZQ series excitation test transformers. 

[image: image2.jpg]



3.3 Schematic drawing of three set of HZJ  series excitation transformers.

[image: image3.jpg]



Explanation：

Control unit will provide power to the primary test winding, at the same time, the end and crust of primary high frequency voltage winding touches the floor, the head will be connected with high frequency voltage’s end and its crust of the secondary test transformer. The primary series excitation switch provides power to the secondary low frequency voltage excitation winding. The same principal can be applied into the tertiary, the output voltage of the tertiary test transformer is the voltages sum of these three test transformer, that’s to say, U(sum)＝u1＋u2＋u3，at the same time, the capacity relationship is S(sum)=s3×3.

3.4  HZ-JZ will form the direct current series excitation test transformer, but we need to add 2 eq \r(2) u silicon stack into the test transformer which is the highest frequency voltage after exchange series excitation.

1. Test transformer should be applied into use with control unit, as for how to use control unit, please see Operation Manual of Control unit.
2. Screening wire should be applied into the direct current test to avoid straying leakage. After test, discharge rod is applied to release the restored electricity.

3. The end of high frequency voltage filtering capacitance should be connected with the ground wire, together with crust of control unit to connect with the earth wire.

4. The whole test should follow the regulation in high frequency voltage test site, should pay more attention to the safety of equipment and body.

[image: image9.png]‘meter

input





HZXC HV Hipot Control Unit (≤10KVA)
Control Box(≤10KVA)

If the capacity of main control box is not more than10KVA the panel of the main control box is as figure 4. 
[image: image4.jpg]L) e e & o & b
Comomm)  Cosumed L

- Zero potential
AC220V Power indicator “°7° BO'Sh Voltage Output-

Operate box

High Voltage

Overcurrent protection

Low voltage current

ON OFF

Time switch

Power Switch Opening





Figure 4 Panel of main control box

The operation of the insulation test with HZJ series HIPOT tester is as follow:

Please make grounding connection for sample object, HV transformer and main control box first

Please discharge the sample object if the sample object is a capacitive equipment.
Please make connection for tester and sample object according to figure 3.
Please make power connection for main control box.
Confirm the high voltage value in withstand. 

Setting the protection value of current by the pointer on the over current protection relay panel.
Adjust the regulator to zero position and then press down the close button on the panel the tester with enable the high voltage output unit.

If the regulator is not at zero position when you press down the close button the high voltage output unit would not be enabled. There is a zero position indication lighter on the panel of the main control box.
Adjust the high voltage output to the withstand test value step by step. Read the high voltage value and LV current from meters at the same time.
Start the timer by the timer switcher on the main control box panel when the high voltage has. 

If the current over the value set on the panel of the over current relay the tester would cut off the power supply of HV transformer immediately. It is said the test result is failure.

If the timer display value reach the set value the tester would have a sound alarm to inform operator that the withstand time is ok. If the tester has not start the over current protection unit before sound alarm it is said the test result is ok.

Open the power supply of HV transformer by press down the “open” button on the panel of the main control box when test is end.
Please discharge the high voltage circuit of sample equipment before remove off the cable connection of high voltage circuit.
Please do not start the test if some part of the tester had been destroyed.

HZTC HV Hipot Control Unit (≥10KVA)
I、Outline

HZTC series control station is a complete set of equipment of high voltage test transformer, it and the test transformer carry out resistance pressure and leakage test. This product is in according with electric industrial standard DL/T848.2-2004.

II、Main Characteristics

This series product has characteristics, such as beautiful appearance, small volume, light weight, simply operation and conveniently maintenance.

This series control station is consists of touch type voltage adjustor and circuit on control, measure and signal. After goes through work frequency power 230V/400V, adjust the output voltage of voltage adjustor(namely the input voltage of test transformer), then accept the required test high voltage(the pressure value which is tester），which work principle is as the follow drawing.
[image: image5.emf]FU2


FU4


HG


HR


FU1


FU3


SP


KM


KM


KO


ST


KM


KM


LJ


TA


LJ


A


L4


L3


TY


L1


L2


KM


KM


V




FU2

FU4

HG

HR

FU1

FU3 SP

KM

KM

KO ST

KM

KM

LJ

TA

LJ A

L4 L3

TY

L1

L2

KM

KM

V


KM  AC Touch Machine      HG、HR Indicator     TY  Auto Voltage Adjustor 

LJ  Current Relay     TA  Current Mutual Inductance    KO  Zero Switch

III、Panel introduction

Series Controller(≥10KVA)

If the capacity of main control box is over 10KVA the panel of the main control box is as following: 
[image: image10.jpg]



[image: image11.jpg]



1、HV voltmeter（KV）  2、LV ammeter（A）  
3、Over current protection setup

4、Power



5、Operate


    6、Withstand voltage time setup

7、Timer
                        8、Over current protection ratio(×1, ×2,OFF)


9、Handle of voltage regulator


10、Start



11、Stop


12、Power Input 220V/380V

13、Output 0~250V/430V

  
    14、Meter               15、Grounding
IV、Technical Parameter
	Model
	Power
	Output

	
	Phase Value
	Voltage（V）
	Frequency（HZ）
	Voltage（V）
	Current（A）

	HZTC-10
	1/2
	230/400
	50
	250/430
	28/16.3

	HZTC-15
	2
	380
	50
	430
	23.3

	HZTC-20
	2
	380
	50
	430
	32.6

	HZTC-30
	2
	380
	50
	430
	46.5

	HZTC-50
	2
	380
	50
	430
	69.8


V、Connection Wire Sketch drawing of It and High Voltage Test Transformer

[image: image6.png]~mostaor)

anzinput]

control unit HV test transformer
meter
8 O rager] 3
w0
o input





VI、Manual Explanation

1．As the table shows, please connect the control station with the test transformer, also please do not forget to connect with the floor line. After careful examination, you can make electricity go through it.

2．When the electricity goes through, please turn the voltage adjustor to Null, Zero Switch turns on and the signal turns on too(which indicate that the output of the voltage adjustor is Zero).

3．Press the Start Button, connect with touch machine, and plug the voltage adjustor in, at the same time, the power signal light will turn off, but working signal light will turn on.

4．Whirl the voltage adjustor slowly and clockwise, and read carefully the voltage meter, when it reaches the required voltage, please stop whirling and change the opposite direction to whirl until it reaches back to Zero.

5．After the examination, please press Stop Button, to shut off the touch machine, and the working signal light will turn off, but the Zero Signal Light will turn on.

6．This equipment is installed with over-current protection. Over-current relay should be chosen when you get the data by examination. But the relay always is setting to be 80% of the rated data. When it look a little over-loaded, please reset it according to the loaded current, to guarantee the safety of this equipment. During the voltage is becoming higher and higher, this experimental equipment will be proved not to be qualified if it becomes short-current, over-loaded relay, and the power were shut down. When it happens, you should whirl the adjustor to Zero Level.

VII、Usage and Maintenance 
1．When you open the box, you need to check whether it’s in good condition or not, especially you need to check whether the connection ports become loose or not, and the carbon brush connects with the voltage adjustor well or not.

2．Strictly follow the procedure, please read the manual first.

3. If it has been not in use for a long time, you should check main circuit floor insulating resistance by 2500V MΩ meter, and the data should not below 1.5MΩ.

VIII、Supplementary Explanation
HZTC series control station is another set of equipment of light test transformer, it has characteristics, perfect capacity, beautify appearance, small volume, light weight, beside, also has the function of switch on and timing, which manual explanation is same as TC control station.

1、Over-current rated value= Over-current relay dial reading ×K
    Among which, K is as a state value of change/excise (-SA) switch of current power, respectively for as 1, 2, ∞., K of the switch in ×1、×2 shift is as 1 and 2 respectively, excise shift is as +∞(in normal condition without using it to avoid damaging the equipment due to lost the protection for transformer.

2、Electric control station is normally above 30KVA. As for client convenience, it adopts the methods of increasing voltage, decreasing voltage. The method of voltage increasing is same as manual, firstly fast, secondly slow. When the required voltage of increasing voltage is coming, don’t press the button forever, it’d better loose a little (press and loose by turns). During the voltage decreasing, press the button of decreasing voltage until charcoal brush back to zero, then the zero signals light is on, you can press the button of stop. Finally, shut off the general switch (air switch).

3、Panel drawing of control station and connection drawing, see the annex.

4、This control station could measure the high voltage leak current of the tester. Please measure the high voltage leak current after accomplish the test of the AC voltage during in using to prevent occurring short circuit phenomenon and produce high voltage which exist dangers for operator. The specific procedure is as following:
First, connect the back connection board of the control station in specific wire, and then carry out the AC voltage test. Second, link the high voltage end part of the control station and test transformer (see the wiring sketch drawing in the next page) namely could read the value of the high voltage current.

[image: image12.jpg]control
.

oy

the back




IX、Electrical schematic diagram
[image: image13.png]